## Sheet1
Commodity : 40 Cusec-10m TDH (Relift Pumping station)
Q'ty : 5 Units
Sr No | DESCRIPTION | SPECIFICATION
1 | Type | Electric Motor-Driven, Single-Stage, Double-Suction, Horizontal Split-Casing Type Centrifugal Pump.
2 | Make & Model | To be mentioned
3 | Country of Origin | PR China
4 | Capacity | 4080 m3 / hr
5 | Total Head | 10 M
6 | Suction Diameter | 700 mm Ø
7 | Discharge Diameter | 500 mm Ø
8 | Method of Installation | Fixed Type
9 | Pump Speed | About 740 rpm
10 | Efficiency | 60% (Min)
11 | Pump Rated Power | 185kw
12 | NPSH Required | Not More Than 4m
13 | Service Intended | Irrigation Pump
14 | Type of Fluid | River Water
15 | Pumping Temperature | 40 ' C
16 | Specific Gravity | 1.0~1.1
17 | Impeller Diameter & Width | To be mentioned
18 | Impeller Type | Enclosed , Double Suction
19 | Impeller Material | Stainless Steel
20 | Casing Material | C.I.
21 | Shaft Material | Carbon Steel
22 | Bearing Type | SKF, Roller Bearing and Ball Bearing
23 | Method of Lubrication | Grease (with Greasing Nipple Attached )
24 | Bearing Housing | To be separable from Main Casing
25 | Pump Drive | Flexible, Directly Coupled
II | MOTOR
26 | Type | TEFC, 380 V , 3 Ø,50 Hz , Squirrel Cage, Induction Motor
27 | Make & Model | To be mentioned
28 | Country of Origin | PR China
29 | Rated Power | 200k W
30 | Motor Speed | About 740 rpm
31 | Motor Insulation Class | F
32 | Motor Protection | IP 54
33 | Starting Current | To be mentioned
34 | Method of Starting | Auto Transformer Type (3 Steps Tap Changer)
III | CONTROL PANEL
35 | Type | Indoor, Cubicle , Complete with the following meters, switches and protection units
(A) Over Current Relay
(B) Under Voltage Relay
( C)Phase Failure Relay
(D) Ampere Meter with selector switch
(E) Volt Meter with selector switch
(F) PF Meter
(G) Frequency meter
(H) Start / Stop Switch for each of the Pump- Motors & Vacuum Pump
(I) MCCB
(J) Complete Wiring Connection Accessories For Motor & Control Panel
(K) Hour Run Meter
36 | Make & Model | To be mentioned
| Country of Origin | To be mentioned
V | ACCESSORIES
38 | Make & Model , Country of Origin of each of the accessories must be mentioned | The following accessories must be provided with each of the pumping units. Make & Model, Country of Origin of each of the Accessories is to be mentioned
| (A) Base Frame | Fixed on the Concrete Floor | 1 Unit
| (B) Flannge Coupling | Flexible Type | 1 Set
| ( C)Smooth Bend | (90 deg.) 700 mm Ø with flanges at both ends | 1 No
| (D) M.S Straight Pipe | 8' Length for suction side, 700 mmØ,with flanges at both ends | 2 Nos
| (E) M.S Straight Pipe | 4' Length for suction side, 700 mmØ, with flanges at both ends | 3 Nos
| (F) Straight Pipe | 4' Length for delivery side,500 mmØ,with flanges at both ends. | 2 Nos
| (G) Straight Pipe | 8' Length for delivery side 500 mmØ,with flanges at both ends. | 2 Nos
| (H) Gate Valve | Fitted on delivery side of pump,500mmØ, Resistance must be 200% of operation pressure . | 1 No
| (I) Check Valve | Fitted on delivery side of pump,500mmØ, Resistance must be 200% of operation pressure . | 1 No
| (J) Expansion Joint. | Rubber Bellows Type 700 mmØ, to be fitted on suction side.Resistance must be 200% of operation pressure . | 1 No
| (K) Expansion Joint | Rubber Bellows Type 500 mmØ, to be fitted on delivery side .Resistance must be 200% of operation pressure. | 1 No
| (L) Priming Vacuum Pump | Electric Motor,Three Phase, with Complete Fittings, Accessories for Priming System , Power and Control Cables. | 1 Unit
|  | (i) Flexible Pipe (10 M) | 1 No
|  | (ii) Ball Valve | 1 No
|  | (iii) Water Tank (Capacity 5 Gals) | 1 No
|  | (iv) Pipe Clip | 4 Nos
|  | (v)3C x 10 mm PVC Cable | 100M
|  | (vi)Breaker | 1 No
|  | (vii)Starter (Built - in Control Panel) | 1 No
| (M) Suitable Pressure Gauges | For delivery side, with Complete Fitting Accessories | 1 No
| (N) Suitable Combined Pressure Gauge | For suction side , with Complete Fitting Accessories | 1 No
|  | (i) Foundation Bolt & Nut (As per Desigin ) | 1 Lot
|  | (ii) Pipe Line Bolt & Nut with washer | 300 Sets
|  | (iii) Gasket | 30 Nos
|  | (iv) Glue | 0.5 gal
| (P) For Each Pump, Complete Fitting & Installation | For Power Cable & Control Cable With Accessories | 1 Lot
|  | (i)0.6/1k V,1Cx240mm2 Power Cable with 2Sets of Termination Kit & 6Nos of Cable Lug | 200M
|  | (ii)0.6/1kV,3Cx2.5mm2 Control Cable with 24Nos of Cable Lug | 30M
|  | (iii)0.6/1kV,1Cx70mm2 Power Cable with 6Nos of Cable Lug | 30M
| (Q)Bell - Mouth | With screen | 1 No
| (R )Air Valve | Single Air Valve (Air Intake & Exhaust), Large Orifice , ABS Float, Without Guide , Pressure must be 1Mpa. | 1No
VI | WEIGHT & DIMESION
For Transportation & Installation Purpose
39 | Pump | To be mentioned
40 | Motor | To be mentioned
41 | Other Heavy Parts | To be mentioned
42 | Total Weight & Dimension | To be mentioned
VII | SPARES
Recommended Spars Parts List (Pump, Motor & Control Panel ) for Running Hour 20000 hr.
43 | Shaft | 1 No for 5 Units
44 | Shaft Sleeve | 1 Set for each pump
45 | Wearing | 1 Set for each pump
46 | Bearing | 1 Roller Bearing & 1 Ball Bearing for each pump
47 | Impeller (Stainless Steel) | 1 No for 5 Units
48 | Soft Packing | 50 kgs for each pump
49 | Fuse Set for control Pannel | 1 Set for each pump
50 | Contact Point | 1 Set for each pump
51 | Flexible Coupling Bush | 1 Set for each pump
VIII | TOOLS
Complete Tools- Pump, Motor , Control Panel & Other Accessories Installed For Pumping System at the Pump Station.
52 | Heavy Duty Puller For Bearing & Pump Pulley | 2 Sets for 5 Units
53 | Grease Gun | 1 Set for each pump
54 | Special Tools | if required (To be mentioned detail list)
55 | Common Tools | 2 Sets for 5 Units
(i) Box Spanner(7~28,30,32,34,36,41,46,55)mm
(ii)Adjustable Wrench (36,46)mm
(iii)Ring & Open End Spanner (24,27,30,36,46)mm
(v)4" Pipe Wrench
(vi)2" Pipe Wrench
(viii)Hammer
(ix)Plier
(x)1' Half Round File
(xi) 1' Flat File
(xii)Chain Block (5 Ton)
(xiii)1' Flat Screw Dirver
(xiv)1' Star Screw Driver
IX | BROCHURES
|  | (A)Tested Performance Curve for the Pump(Q-H,Q-Eff;Q-P;Q-NPSH) to be provided. (In English) | 3 Sets
|  | (B)Pump Technical Specification Catalogue to be provided.( In English) | 3 Sets
|  | ( C) Operating & Maintenance Manual (In English) for each pump to be provided. | 3 Sets
|  | (D) Part Catalogue to be provided. (In English ) | 3 Sets
|  | (E) Test Certificate (in English) for each of the pumping unit | 3 Sets
X | ASSEMBLING, TESTING & COMMISSIONING OF PUMPS | Under the Supervision of Manufacturers' Technicians at Seller Expense
XI | GUARANTEE | One Year after Commissioning of the Pumps
XII | Delivery Period | To be mentioned