PROCUREMENT OF AIR FILTER FOR SAIDPUR 20 MW

Price Schedule for Goods (Form PG4-2C)

Goods offered from abroad

Invitation for Tender No:														Date of Tender

Tender Package No:

| GOODS REQUIRED |  |  |  | PRICE OFFERED IN FOREIGN CURRENCY (C & F) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |
| Item No. | Description of Item | Reference Manufacturer’s spares parts list of catalogue | Qty of units Req’d | Unit Price (C & F Price) (Indicate Currency) | Total Price for Item (Col. 4x5) | Amount of Duty and other taxes already Paid (%age of Col. 5) (Not Applicable) | Sales and other taxes payable if Contract is awarded (Not Applicable) | Inland transportation and other local costs for delivery (BD. Tk) | Total Price for Item |  |
|  |  |  |  |  |  |  |  |  | (F/C) | (L/C) |
| Tenderer to state currency of offer |  |  |  |  |  |  |  |  |  |  |
| 1. | PRIMARY AIR FILTER OR PRE-FILTER PAD FOR TURBINE. Size: 24” x 24” x 4” | FCM10A0405 | 1800 pcs |  |  |  |  |  |  |  |
| 2. | PRIMARY AIR FILTER OR PRE-FILRER PAD FOR GENERATOR. Size: 24” x 24” x 2” | FCM10A4023 | 500 pcs |  |  |  |  |  |  |  |
| 3. | SECONDARY IR FILTER BOX OR HIGH EFFICIENCY FILTERS FOR TURBINE Size: 24” x 24” x 12” | FFX9JE5001 | 1000 pcs |  |  |  |  |  |  |  |
|  | Point of Delivery of the Lot |  |  |  |  |  |  | Saidpur Power Station Store, Saidpur |  |  |
|  | Delivery Period for the Lot |  |  |  |  |  |  | 180 Days from the date of opening of L/C |  |  |
|  | Sub-Total Price Lot: |  |  |  |  |  |  |  |  |  |
|  | The Currencies used in the above prices are: |  |  | Total Price |  |  |  |  |  |  |
|  | Name of Tenderer & |  |  | Signature of Tender & Date: |  |  |  |  |  |  |

Technical Specifications

Air Filter for Saidpur 20 MW

Frame 5000 IP, Model PG 5361, Sl No. T-2197T-242 manufactured by Alsthom, France

Power Station and Climatic Condition:

1.	Name of Power Station		:	Saidpur 20 MW Gas Turbine Power Station.

2.	Unit No.				:	1

3.	Total air flow of each unit		:	436 tons/hr

4.	Total Filtration area			:	(a) For Turbine 360 sft

(b) For Generator 48 sft

5.	Temperature range			:	+ 5 deg C to 45 deg C

6.	Weather condition			:	Typical High Humidity (90%),

Insects, Flies, Mosquitoes,

7.	Place of use				:	Turbine & Generator Intake.

8.	Type of Filter				:	Disposable pad & box.

9.	Number of stage			:	2 (Two)

(Pre filter pad & high efficiency filter box)

10.	Type of dust				:	Dry, Moistured, Corrosive, Sooty-Oily, erosive.

A.	SPECIFICATION OF PRIMARY AIR FILTER OR PRE-FILTER PAD FOR TURNBINE:

| Sl. No. | Description | BPDB’s Requirement | Tenderer’s Offer (To be filled by Tenderer) |
| --- | --- | --- | --- |
| 1. | Manufacturer’s Name | To be mentioned by the Tenderer. |  |
| 2. | Year of manufacturer | To be mentioned by the Tenderer. |  |
| 3. | Country of Origin | To be mentioned by the Tenderer. |  |
| 4. | Size | 24” x 24” x 4” (4” pad will be compressed to 2” for installation) |  |
| 5. | No. of Cells | 90 Nos. |  |
| 6. | Type | Disposable (Adhesive impregnated glass |  |
| 7. | Model No. | To be mentioned by the Tenderer |  |
| 8. | Filter Media | Filter pads are made of continuous glass fiber/ synthetic fiber with no voids or other spots & impregnated with correct amount of fire retardant and non migrating adhesive. |  |
| 9. | Filter Materials | Glass fiber / synthetic fiber. |  |
| 10. | Air flow rate of each cell/pad | 2000 CFM or 3400 Cu-M/ hr (at air velocity 500ft/min.) |  |
| 11. | Initial resistance at rated air flow | 75 Pa (0.3 inch W.G) |  |
| 12 | Final resistance oat rated air flow | 250 Pa (1.0 inch W.G) |  |
| 13. | Average dust weight arrestance on AC fine test dust | 99% |  |
| 14. | Dust holding capacity at final resistance on AC fine test dust | Min. 1000gms. |  |
| 15. | Lowest Particie Size | upto 5 microns. |  |
| 16. | Max. front velocity | 10 ft/sec |  |

| 17 | Direction of air flow | Filter media should be properly marked to identify the direction of air flow. |  |
| --- | --- | --- | --- |

B. SPECIFICATION OF PRIMARY AIR FILTER OR PRE-FILTERS FOR GENRATOR:

| Sl. No. | Description | BPDB’s Requirement | Tenderer’s Offer (To be filled by Tenderer) |
| --- | --- | --- | --- |
| 1. | Manufacturer’s name | To be mentioned by the Tenderer |  |
| 2. | Year of Manufacturer | To be mentioned by the Tenderer |  |
| 3. | Country of origin | To be mentioned by the Tenderer |  |
| 4. | Size | 24” x 24” x 2” |  |
| 5. | No. of Cells | 12 Nos. |  |
| 6. | Type | Disposable (adhesive impregnated glass fibre pad) |  |
| 7. | Model No. | To be mentioned by the Tenderer. |  |
| 8. | Filter media | Filter pads are made of continuous glass fibre / synthetic fibre with correct amount of fire retardant and non-migrating adhesive. |  |
| 9. | Filter materials | Glass fibre / synthetic fibre. |  |
| 10. | Temperature limit | 100oC |  |
| 11. | Air F low rate each cell / ped | 2000 CFM or 3400 M3 / hr (at air velocity 500 ft / min) |  |
| 12. | initial resistance at rated air flow | 50 Pa (0.2 inch W.G) |  |
| 13. | Final resistance at rated air flow. | 250 Pa (1.0 inch W.G) |  |
| 14. | Average dust weight arrestance | 99% |  |
| 15. | Dust holding capacity at final resistance on A.C. fine test dust | Min. 1000 gms. |  |
| 16. | Lowest particle size | 5 Microns. |  |

C .SPECIFICATION OF SECONDARY AIR FILTER OR HIGHEFFICIENCY FILTER FOR TURBINE:

| Sl. No. | Description | BPDB’s Requirement | Tenderer’s Offer (To be filled by Tenderer) |
| --- | --- | --- | --- |
| 1. | Manufacturer’s name | To be mentioned by the Tenderer. |  |
| 2. | Year of Manufacturer | To be mentioned by the Tenderer. |  |
| 3. | Country of origin | To be mentioned by the Tenderer. |  |
| 4. | Size | 24” x 24” x 12” |  |
| 5. | No. of Cells | 90 Nos. |  |
| 6. | Type | High efficiency cartridge type air filter (box). |  |
| 7. | Cell / Cartridge weight | To be mentioned by the Tenderer |  |
| 8. | Model No. | To be mentioned by the Tenderer |  |

| 9. | Cell sides | Galvanized Metal / Aluminum / Plastic (further enhanced with galvanized wire mesh). |  |
| --- | --- | --- | --- |
| 10. | Separators in filler media | Filter media folded between corrugated aluminum / plastic separator. |  |
| 11. | Face guards | Permanently affixed to air entering sides & air leaving sides. (Assembly of the galvanized metal / plastic housing is accomplished by a unique mechanical interlocking system that eliminates rivets or nuts and bolts) |  |
| 12. | Header | Single header (flanged galvanized steel / plastic) at air entering side of the filter (No use of screw or nut bolt). |  |
| 13. | Filter materials / media | Ultra fine Glass fiber/synthetic fiber. |  |
| 14. | Area of Filter material / media used per cell | To be mentioned by the Tenderer |  |
| 15. | Air flow rate of each cell / pad. | 2000 CFM or 3400 m3 / hr (at air velocity 500 ft/min. |  |
| 16. | Initial resistance at rated air flow | 165 Pa (0.66inch W.G) |  |
| 17. | Final resistance at rated air flow | 625 Pa (2.5 inch W.G) |  |
| 18. | Average atmospheric dust spot efficiency on ASHRAE test dust | Min 88% |  |
| 19. | Average dust weight Arrestance on ASHRAE test dust | 99% |  |
| 20. | Dust holding capacity at final resistance on ASHRAE test dust | 900 gms. |  |
| 21. | Lowest particle Size | 3 Microns. |  |

BID BOND / BID SECURITY

US$ 1000.00 (BDTK. 70,000.00).

OFFER VALIDITY

120 (One Hundred Twenty) days respectively from the date of opening of tender.

VALIDITY OF SHIPMENT

180 (One Hundred Eighty Days) from the date of opening of L/C.